## Sheet2
HHA to Eplus Dictionary
HHA Object: | ZONES | Zone Name | Zone TemplGroup | Zone TemplName | Area/Ceilng | Max Ceiling | Max Ceiling Prev | Dsn Space Clg Temp | Dsn Space Clg Temp Prev | Dsn Space Clg RH | Dsn Space Clg RH Prev | Dsn Space Htg Temp | Dsn Space Htg Temp Prev | Dsn Space Htg RH | Dsn Space Htg RH Prev | Dsn SA Clg Temp | Dsn SA Clg Temp Prev | Dsn SA Clg Humid | Dsn SA Clg Humid Prev | Dsn SA Htg Temp | Dsn SA Htg Temp Prev | Dsn SA Htg Humid | Dsn SA Htg Humid Prev | Min OA ACH | Min OA ACH Prev | Min OA Rp | Min OA Rp Prev | Min OA Ra | Min OA Ra Prev | OA EZ Vent Eff | OA EZ Vent Eff Prev | Min SA L/S/m2 | Min SA L/S/m2 Prev | Min SA ACH | Min SA ACH Prev | Min Exh L/S | Min Exh L/S Prev | Min Exh ACH | Min Exh ACH Prev | Inf Clg Dsn ACH | Inf Clg Dsn ACH Prev | Inf Clg Dsn L/S/m2 | Inf Clg Dsn L/S/m2 Prev | Inf Htg Dsn ACH | Inf Htg Dsn ACH Prev | Inf Htg Dsn L/S/m2 | Inf Htg Dsn L/S/m2 Prev | Light Pwr | Light Pwr Prev | Light Unit | Light Unit Prev | Light %RA | Light %RA Prev | TaskLgt Pwr | TaskLgt Pwr Prev | TaskLgt Unit | TaskLgt Unit Prev | Occ Num | Occ Num Prev | Occ Unit | Occ Unit Prev | Occ Met | Occ Met Prev | Occ SHR | Occ SHR Prev | Equip Pwr | Equip Pwr Prev | Equip Unit | Equip Unit Prev | Equip SHR | Equip SHR Prev
| ScheduleTypeLimits_Any Number | 'Any Number' | '' | '' | ''
Eplus Class: | ScheduleTypeLimits | A1 | N1 | N2 | A2
| ScheduleTypeLimits_Fraction | 'Fraction' | 0 | 1 | 'CONTINUOUS'
Eplus Class: | ScheduleTypeLimits | A1 | N1 | N2 | A2
| ScheduleTypeLimits_On/Off | 'On/Off' | 0 | 1 | 'DISCRETE'
Eplus Class: | ScheduleTypeLimits | A1 | N1 | N2 | A2
| ScheduleTypeLimits_Control Type | 'Control Type' | 0 | 4 | 'DISCRETE'
Eplus Class: | ScheduleTypeLimits | A1 | N1 | N2 | A2
| ScheduleTypeLimits_Temperature | 'Temperature' | -60 | 200 | 'CONTINUOUS'
Eplus Class: | ScheduleTypeLimits | A1 | N1 | N2 | A2
| ScheduleTypeLimits_Humidity | 'Humidity' | 10 | 90 | 'CONTINUOUS'
Eplus Class: | ScheduleTypeLimits | A1 | N1 | N2 | A2
| Light Pwr | [Zone Name]+'_Lights' | [Zone Name] | 'BLDG_LIGHT_SCH_'+[Zone TemplGroup]+' : '+[Zone TemplName] | [Light Unit]=='W'?'LightingLevel': ([Light Unit]=='W/m2'?'Watts/Area': ([Light Unit]=='W/occ'?'Watts/Person':'')) | [Light Unit]=='W'?[Light Pwr]:'' | [Light Unit]=='W/m2'?[Light Pwr]:'' | [Light Unit]=='W/occ'?[Light Pwr]:'' | [Light %RA] | 0.7 | 0.2 | 1
Eplus Class: | Lights | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | N6 | N7
| Templ Light Pwr | [Zone TemplGroup]+' : '+[Zone TemplName]+'_Lights' | 'ZoneList3_Light_'+[Zone TemplGroup]+' : '+[Zone TemplName] | 'BLDG_LIGHT_SCH_'+[Zone TemplGroup]+' : '+[Zone TemplName] | [Light Unit]=='W'?'LightingLevel': ([Light Unit]=='W/m2'?'Watts/Area': ([Light Unit]=='W/occ'?'Watts/Person':'')) | [Light Unit]=='W'?[Light Pwr]:'' | [Light Unit]=='W/m2'?[Light Pwr]:'' | [Light Unit]=='W/occ'?[Light Pwr]:'' | [Light %RA] | 0.7 | 0.2 | 1
Eplus Class: | Lights | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | N6 | N7
| TaskLgt Pwr | [Zone Name]+'_TaskLgt' | [Zone Name] | 'BLDG_TASKLGT_SCH_'+[Zone TemplGroup]+' : '+[Zone TemplName] | [TaskLgt Unit]=='W'?'LightingLevel': ([TaskLgt Unit]=='W/m2'?'Watts/Area': ([TaskLgt Unit]=='W/occ'?'Watts/Person':'')) | [TaskLgt Unit]=='W'?[TaskLgt Pwr]:'' | [TaskLgt Unit]=='W/m2'?[TaskLgt Pwr]:'' | [TaskLgt Unit]=='W/occ'?[TaskLgt Pwr]:'' | 0 | 0.7 | 0.2 | 1
Eplus Class: | Lights | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | N6 | N7
| Templ TaskLgt Pwr | [Zone TemplGroup]+' : '+[Zone TemplName]+'_TaskLgt' | 'ZoneList4_TaskLgt_'+[Zone TemplGroup]+' : '+[Zone TemplName] | 'BLDG_TASKLGT_SCH_'+[Zone TemplGroup]+' : '+[Zone TemplName] | [TaskLgt Unit]=='W'?'LightingLevel': ([TaskLgt Unit]=='W/m2'?'Watts/Area': ([TaskLgt Unit]=='W/occ'?'Watts/Person':'')) | [TaskLgt Unit]=='W'?[TaskLgt Pwr]:'' | [TaskLgt Unit]=='W/m2'?[TaskLgt Pwr]:'' | [TaskLgt Unit]=='W/occ'?[TaskLgt Pwr]:'' | 0 | 0.7 | 0.2 | 1
Eplus Class: | Lights | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | N6 | N7
| ActivityLvSch | A1: 'ActivityLvSch_Met:’+[Occ Met]; A2: 'Any Number'; A3: [Occ Met]
Eplus Class: | Schedule:Constant | A1: A1; A2: A2; A3: N1
| Occ Num | [Zone Name]+'_People' | [Zone Name] | 'BLDG_PEOPLE_SCH_'+[Zone TemplGroup]+' : '+[Zone TemplName] | [Occ Unit]=='occ'?'People': ([Occ Unit]=='occ/m2'?'People/Area': ([Occ Unit]=='m2/occ'?'Area/People':'')) | [Occ Unit]=='occ'?[Occ Num]:'' | [Occ Unit]=='occ/m2'?[Occ Num]:'' | [Occ Unit]=='m2/occ'?[Occ Num]:'' | 0.3 | [Occ SHR] | 'ActivityLvSch_Met:’+[Occ Met]
Eplus Class: | People | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | A5
| Templ Occ Num | [Zone TemplGroup]+' : '+[Zone TemplName]+'_People' | 'ZoneList5_People_'+[Zone TemplGroup]+' : '+[Zone TemplName] | 'BLDG_PEOPLE_SCH_'+[Zone TemplGroup]+' : '+[Zone TemplName] | [Occ Unit]=='occ'?'People': ([Occ Unit]=='occ/m2'?'People/Area': ([Occ Unit]=='m2/occ'?'Area/People':'')) | [Occ Unit]=='occ'?[Occ Num]:'' | [Occ Unit]=='occ/m2'?[Occ Num]:'' | [Occ Unit]=='m2/occ'?[Occ Num]:'' | 0.3 | [Occ SHR] | 'ActivityLvSch_Met:’+[Occ Met]
Eplus Class: | People | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | A5
| Equip Pwr | [Zone Name]+'_PlugEquip' | [Zone Name] | 'BLDG_PLUGEQUIP_SCH_'+[Zone TemplGroup]+' : '+[Zone TemplName] | [Equip Unit]=='W'?'EquipmentLevel': ([Equip Unit]=='W/m2'?'Watts/Area': ([Equip Unit]=='W/occ'?'Watts/Person':'')) | [Equip Unit]=='W'?[Equip Pwr]:'' | [Equip Unit]=='W/m2'?[Equip Pwr]:'' | [Equip Unit]=='W/occ'?[Equip Pwr]:'' | 1-[Equip SHR] | 0.5 | 0
Eplus Class: | ElectricEquipment | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | N6
| Templ Equip Pwr | [Zone TemplGroup]+' : '+[Zone TemplName]+'_PlugEquip' | 'ZoneList6_PlugEquip_'+[Zone TemplGroup]+' : '+[Zone TemplName] | 'BLDG_PLUGEQUIP_SCH_'+[Zone TemplGroup]+' : '+[Zone TemplName] | [Equip Unit]=='W'?'EquipmentLevel': ([Equip Unit]=='W/m2'?'Watts/Area': ([Equip Unit]=='W/occ'?'Watts/Person':'')) | [Equip Unit]=='W'?[Equip Pwr]:'' | [Equip Unit]=='W/m2'?[Equip Pwr]:'' | [Equip Unit]=='W/occ'?[Equip Pwr]:'' | 1-[Equip SHR] | 0.5 | 0
Eplus Class: | ElectricEquipment | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | N6
| ZoneInfiltration Sch | A1: 'InfiltrationSch’; A2: 'Any Number'; A3: 1
Eplus Class: | Schedule:Constant | A1: A1; A2: A2; A3: N1
| ZoneInfiltration:DesignFlowRate_ACH | [Zone Name]+'_ZoneInfil' | [Zone Name] | 'InfiltrationSch’ | 'AirChanges/Hour' | '' | '' | '' | [Inf Htg Dsn ACH] | 1 | 0 | 0 | 0
Eplus Class: | ZoneInfiltration:DesignFlowRate | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | N6 | N7 | N8
| ZoneInfiltration:DesignFlowRate_L/s/m2 | [Zone Name]+'_ZoneInfil' | [Zone Name] | 'InfiltrationSch’ | 'Flow/ExteriorWallArea' | '' | '' | [Inf Htg Dsn L/S/m2]/1000 | '' | 1 | 0 | 0 | 0
Eplus Class: | ZoneInfiltration:DesignFlowRate | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | N6 | N7 | N8
| Templ_ZoneInfiltration:DesignFlowRate | [Zone TemplGroup]+' : '+[Zone TemplName]+'_ZoneInfil' | [Zone Name] | 'InfiltrationSch’ | 'AirChanges/Hour' | '' | '' | '' | [Inf Htg Dsn ACH] | 1 | 0 | 0 | 0
Eplus Class: | ZoneInfiltration:DesignFlowRate | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | N5 | N6 | N7 | N8
| DesignSpecification:OutdoorAir_ACH | A1: [Zone Name]+'_DsnSpec.OA'; A2: 'AirChanges/Hour'; A3: ''; A4: ''; N1: ''; N2: [Min OA ACH]
Eplus Class: | DesignSpecification:OutdoorAir | A1 | A2 | N1 | N2 | N3 | N4
| DesignSpecification:OutdoorAir_RpRa | [Zone Name]+'_DsnSpec.OA' | 'Sum' | [Min OA Rp]/1000 | [Min OA Ra]/1000 | '' | ''
Eplus Class: | DesignSpecification:OutdoorAir | A1 | A2 | N1 | N2 | N3 | N4
|  | 'DsnSpec.ZnAirDist_Ez:'+[OA EZ Vent Eff] | [OA EZ Vent Eff] | [OA EZ Vent Eff]
Eplus Class: | DesignSpecification:ZoneAirDistribution | A1: A1; A2: N1; N1: N2
|  | [Zone Name] | 'SupplyAirTemperature' | [Dsn SA Clg Temp] | '' | 'SupplyAirTemperature' | [Dsn SA Htg Temp] | '' | [Dsn SA Clg Humid] | [Dsn SA Htg Humid] | [Zone Name]+'_DsnSpec.OA' | '' | '' | 'DesignDay' | '' | '' | '' | '' | 'DesignDay' | '' | '' | '' | '' | 'DsnSpec.ZnAirDist_Ez:'+[OA EZ Vent Eff]
Eplus Class: | Sizing:Zone | A1 | A2 | N1 | N2 | A3 | N3 | N4 | N5 | N6 | A4 | N7 | N8 | A5 | N9 | N10 | N11 | N12 | A6 | N13 | N14 | N15 | N16 | A7
| SingleHtgSetPt_Sch | A1: 'SingleHtgSetPt_Sch_'+[Dsn Space Htg Temp]+'C'; A2: 'Temperature'; N1: [Dsn Space Htg Temp]
Eplus Class: | Schedule:Constant | A1: A1; A2: A2; N1: N1
| SingleHtgSetPt | A1: 'SingleHtgSetPt_'+[Dsn Space Htg Temp]; A2: 'SingleHtgSetPt_Sch_'+[Dsn Space Htg Temp]+'C'
Eplus Class: | ThermostatSetpoint:SingleHeating | bar: A1 to A2
| ControlTypeSch_SingleHtg | A1: 'ControlTypeSch_SingleHtg’; A2: 'Control Type'; N1: 1
Eplus Class: | Schedule:Constant | A1: A1; A2: A2; N1: N1
| Tstat_SingleHtg | [Zone Name]+'_Tstat' | [Zone Name] | 'ControlTypeSch_SingleHtg’ | 'ThermostatSetpoint:SingleHeating' | 'SingleHtgSetPt_'+[Dsn Space Htg Temp]
Eplus Class: | ZoneControl:Thermostat | A1 | A2 | A3 | A4 | A5
| Templ Tstat_SingleHtg | [Zone TemplGroup]+' : '+[Zone TemplName]+'_Tstat' | 'ZoneList7_TstatSingleHtg_'+[Zone TemplGroup]+' : '+[Zone TemplName] | 'ControlTypeSch_SingleHtg’ | 'ThermostatSetpoint:SingleHeating' | 'SingleHtgSetPt_'+[Dsn Space Htg Temp]
Eplus Class: | ZoneControl:Thermostat | A1 | A2 | A3 | A4 | A5
| SingleClgSetPt_Sch | A1: 'SingleClgSetPt_Sch_'+[Dsn Space Clg Temp]+'C'; A2: 'Temperature'; N1: [Dsn Space Clg Temp]
Eplus Class: | Schedule:Constant | A1: A1; A2: A2; N1: N1
| SingleClgSetPt | A1: 'SingleClgSetPt_'+[Dsn Space Htg Temp]; A2: 'SingleClgSetPt_Sch_'+[Dsn Space Clg Temp]+'C'
Eplus Class: | ThermostatSetpoint:SingleCooling | bar: A1 to A2
| ControlTypeSch_SingleClg | A1: 'ControlTypeSch_SingleClg’; A2: 'Control Type'; N1: 2
Eplus Class: | Schedule:Constant | A1: A1; A2: A2; N1: N1
| Tstat_SingleClg | [Zone Name]+'_Tstat' | [Zone Name] | 'ControlTypeSch_SingleClg’ | 'ThermostatSetpoint:SingleCooling' | 'SingleClgSetPt_'+[Dsn Space Htg Temp]
Eplus Class: | ZoneControl:Thermostat | A1 | A2 | A3 | A4 | A5
| Templ Tstat_SingleClg | [Zone TemplGroup]+' : '+[Zone TemplName]+'_Tstat' | 'ZoneList8_TstatSingleClg_'+[Zone TemplGroup]+' : '+[Zone TemplName] | 'ControlTypeSch_SingleClg’ | 'ThermostatSetpoint:SingleCooling' | 'SingleClgSetPt_'+[Dsn Space Htg Temp]
Eplus Class: | ZoneControl:Thermostat | A1 | A2 | A3 | A4 | A5
|  | 'DualSetPt_'+[Dsn Space Htg Temp] | 'SingleHtgSetPt_Sch_'+[Dsn Space Htg Temp]+'C' | 'SingleClgSetPt_Sch_'+[Dsn Space Clg Temp]+'C'
Eplus Class: | ThermostatSetpoint:DualSetpoint | A1: A1; A2: A2; N1: A3
| ControlTypeSch_DualSetPt | A1: 'ControlTypeSch_DualSetPt’; A2: 'Control Type'; N1: 4
Eplus Class: | Schedule:Constant | A1: A1; A2: A2; N1: N1
| Tstat_DualSetPt | [Zone Name]+'_Tstat' | [Zone Name] | 'ControlTypeSch_DualSetPt’ | 'ThermostatSetpoint:DualSetpoint' | 'DualSetPt_'+[Dsn Space Htg Temp]
Eplus Class: | ZoneControl:Thermostat | A1 | A2 | A3 | A4 | A5
| Templ Tstat_DualSetPt | [Zone TemplGroup]+' : '+[Zone TemplName]+'_Tstat' | 'ZoneList9_TstatDualSetPt_'+[Zone TemplGroup]+' : '+[Zone TemplName] | 'ControlTypeSch_DualSetPt’ | 'ThermostatSetpoint:DualSetpoint' | 'DualSetPt_'+[Dsn Space Htg Temp]
Eplus Class: | ZoneControl:Thermostat | A1 | A2 | A3 | A4 | A5
| MinRelHumSetSch | A1: 'MinRelHumSetSch_'+[Dsn Space Htg RH]+'%'; A2: 'Humidity'; N1: [Dsn Space Htg RH]
Eplus Class: | Schedule:Constant | A1: A1; A2: A2; N1: N1
| MaxRelHumSetSch | A1: 'MaxRelHumSetSch_'+[Dsn Space Clg RH]+'%'; A2: 'Humidity'; N1: [Dsn Space Clg RH]
Eplus Class: | Schedule:Constant | A1: A1; A2: A2; N1: N1
|  | [Zone Name]+'_Humidistat' | [Zone Name] | 'MinRelHumSetSch_'+[Dsn Space Htg RH]+'%' | 'MaxRelHumSetSch_'+[Dsn Space Clg RH]+'%'
Eplus Class: | ZoneControl:Humidistat | A1 | A2 | A3 | A4
|  | [Zone Name]+'_IdealLoadsAirSystem' | '' | [Zone Name]+'_Air Supply Node' | [Zone Name]+'_Air Exhaust Node' | [Dsn SA Htg Temp] | [Dsn SA Clg Temp] | [Dsn SA Htg Humid] | [Dsn SA Clg Humid] | 'NoLimit' | '' | '' | 'NoLimit' | '' | '' | '' | '' | 'Humidistat' | '' | 'Humidistat' | [Zone Name]+'_DsnSpec.OA' | '' | 'None' | 'NoEconomizer' | 'None' | 0.7 | 0.65
Eplus Class: | ZoneHVAC:IdealLoadsAirSystem | A1 | A2 | A3 | A4 | N1 | N2 | N3 | N4 | A5 | N5 | N6 | A6 | N7 | N8 | A7 | A8 | A9 | N9 | A10 | A11 | A12 | A13 | A14 | A15 | N10 | N11
|  | [Zone Name]+'_Primary Air Terminal' | [Zone Name]+'_Primary Air Terminal' Discharge Node' | 'AirTerminal:SingleDuct:VAVReheat' | [Zone Name]+'_VAV Reheat Terminal Device'
Eplus Class: | ZoneHVAC:AirDistributionUnit | A1: A1; A2: A2; A3: A3; A4: A4
|  | [Zone Name]+'_ZoneHVACEquipment' | [Zone Name]+'_IdealLoadsAirSystem' | [Zone Name]+'_Primary Air Terminal' | 1 | 1
Eplus Class: | ZoneHVAC:EquipmentList | A1: A1; A2: A2; A3: A3; A4: N1; N1: N2
|  | [Zone Name] | [Zone Name]+'_ZoneHVACEquipment' | [Zone Name]+'_Air Supply Node' | [Zone Name]+'_Air Exhaust Node' | [Zone Name]+'_HVAC Primary Air and HVAC Equipment Node' | [Zone Name]+'_R/A Duct Connection Node'
Eplus Class: | ZoneHVAC:EquipmentConnections | A1 | A2 | A3 | A4 | A5 | A6
| NodeList_SupplyAirNode | A1: [Zone Name]+'_Air Supply Node'; A2: [Zone Name]+'_Primary Air Terminal Discharge Node'
Eplus Class: | NodeList | bar: A1 to A2
| NodeList_ExhaustAirNode | A1: [Zone Name]+'_Air Exhaust Node'; A2: [Zone Name]+'_Zone Exhaust Node'
Eplus Class: | NodeList | bar: A1 to A2