## CRITERIA
| SysLoad. ID |  | SysLoad. Name | SysLoad. IsTempl%% | SysLoad. NumZones%%SysLoad.Area | SysLoad. TemplName |  |  | SysLoad. Type |  | SysLoad. FanPosition |  | SysLoad. Configuration | [13 empty] | SysLoad. Divrst.Lights | SysLoad. Divrst.Lightsprev | SysLoad. Divrst.Tskltg | SysLoad. Divrst.Tskltgprev | SysLoad. Divrst.Occ | SysLoad. Divrst.Occprev | SysLoad. Divrst.Equip | SysLoad. Divrst.Equipprev | SysLoad. SF.TSP | SysLoad. SF.TSPprev | SysLoad. SF.StEff | SysLoad. SF.StEffprev | SysLoad. SF.DrLoss | SysLoad. SF.DrLossprev | SysLoad. SF.MinMotorSF | SysLoad. SF.MinMotorSFprev | SysLoad. RF.TSP | SysLoad. RF.TSPprev | SysLoad. SF.StEff | SysLoad. SF.StEffprev | SysLoad. RF.DrLoss | SysLoad. RF.DrLossprev | SysLoad. RF.MinMotorSF | SysLoad. RF.MinMotorSFprev | SysLoad. EA.Calc | SysLoad. EA.Calcprev | SysLoad. EA.CalcValue | SysLoad. EA.CalcValueprev | SysLoad. EA.AvgWperL/s | SysLoad. EA.AvgWperL/sprev | SysLoad. OA.CalcMethod | SysLoad. OA.CalcMethodprev | SysLoad. MinOA | SysLoad. MinOAprev | SysLoad. MaxOA | SysLoad. MaxOAprev | SysLoad. HumdfrLvgW | SysLoad. HumdfrLvgWprev | SysLoad. HumdfrLoss | SysLoad. HumdfrLossprev | SysLoad. HR.SensEff | SysLoad. HR.SensEffprev | SysLoad. HR.LatEff | SysLoad. HR.LatEffprev | SysLoad. PHC.EntAirTemp | SysLoad. PHC.EntAirTempprev |  | SysLoad. PHC.LvgAirTemp | SysLoad. PHC.LvgAirTempprev | SysLoad. HC.EntAirTemp |  |  | SysLoad. HC.LvgAirTemp | SysLoad. HC.LvgAirTempprev | SysLoad. CC.EntAirTemp | SysLoad. CC.EntAirTempprev |  | SysLoad. CC.LvgAirTemp | SysLoad. CC.LvgAirTempprev | SysLoad. CC.EntAirHum | SysLoad. CC.EntAirHumprev |  | SysLoad. CC.LvgAirHum | SysLoad. CC.LvgAirHumprev | SysLoad. CC.HumSetpt | SysLoad. CC.HumSetptprev | SysLoad. CalcMethod.PHC | SysLoad. CalcMethod.HC | SysLoad. CalcMethod.CC | SysLoad. CalcMethod.Humdfr
| SYSTEMS: | [7 empty] | TYPE AND CONFIGURATION | [17 empty] | SYSTEM LOAD CALCULATION CRITERIA
[27 empty] | Diversity Factor | [7 empty] | Supply Fan | [7 empty] | Return Fan | [7 empty] | Exhaust | [5 empty] | O/A & Humidity Control | [9 empty] | Recovery | [6 empty] | Heating & Cooling Coils
| Sys # |  | System Name |  | # Zones Area | Template |  |  | System Type |  | Fan Position |  | Code |  | Component Order | [11 empty] | Lights |  | Task Lights |  | Occupant |  | Equipment |  | Fan T.S.P. |  | Static Efficiency |  | Drive Loss |  | Minimum Motor S.F. |  | Fan T.S.P. |  | Static Efficiency |  | Drive Loss |  | Minimum Motor S.F. |  | Exh Air Calculation |  | E/A Calc Value |  | Avg. Power W per L/s |  | Minimum O/A Calculation Method |  | Min O/A |  | Max O/A |  | Humidifier Leaving W |  | Humidifier Losses |  | H/R Sens Eff |  | H/R Latent Eff |  | PH/C Entering Air Temp. |  |  | PH/C Leaving Air Temperature |  | H/C Entering Air Temperature |  |  | H/C Leaving Air Temperature |  | Entering Air Temperature |  |  | C/C Leaving Air Temperature |  | Entering Air Humidity (W) |  |  | C/C Leaving Air Humidity (W) |  | R/A Humidity Setpoint (W) |  | Component Capacity Reduction by Heat Recovery. Assume for each component sizing is based on:
[35 empty] | Pa | [7 empty] | Pa | [19 empty] | kgW/kgA | [7 empty] | OC |  |  | OC |  | OC |  |  | OC |  | OC |  |  | OC |  | kgW/kgDA |  |  | kgW/kgDA |  | kgW/kgDA |  | PH/C | H/C | C/C | HUM
| Field 1 |  | 2 |  | 3 | 4 |  |  |  |  | 3 |  |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 4 |  | 5 | [5 empty] | 5 |  | 5 |  | 6 |  | 7 |  | 7 |  | 8 |  | 9 |  | 10 |  | 1 |  | 1 |  | 2 |  | 1 |  | 1 |  | 1 |  | 2 |  |  |  |  | 3 | 4 |  |  | 5 | 6 |  | 7 | 8 | 9 | 10 |  |  | 11 | 12 | 13 |  |  | 14 |  | 15 |  | 15 |  |  | 16 |  | 17 | 18 | 19 | 20
4 | 0 |  | 1 | 2 | 3 | 4 | 5 | 6 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 71 | 72 | 73 |  | 75 | 76 | 77 | 78 |  | 80 | 81 | 82 | 83 | 84 |  | 86 | 87 | 88 |  | 90 | 91 |  | 93 |  | 96 | 97 | 98 | 99
|  | FALSE | Template MUA | TRUE |  |  | FALSE | Template MUA | MU/A-HTG-CLG-H/RCV | MU/A-HTG-CLG-H/RCV | DRAW THRU C/C | DRAW THRU C/C | 8M | 8M | [11 empty] | 26: TRUE; 27: 0.88; 28: 0.78; 29: 0.25; 31: 1; 33: 0.33; 35: 1800; 37: 0.65; 39: 0.06; 41: 1.2; 43: 1200; 45: 0.65; 47: 0.065; 49: 1.2 | Dsgn Frac |  | 1 |  | 1 |  | 0.0004 | 0.0004 | 0.015 | 0.015 | 0.7 | 0.75 | 0.7 | 0.72 | Calc |  | Calc | 5 |  | Calc |  | Calc | 13 |  | Calc |  | Calc | 12.5 | 5 | 0.013 | 0.0005 | Calc | 0.006 | 0.0004 | 0.011
|  |  |  | TRUE |  |  | FALSE |  |  | FALSE |  | TRUE |  | TRUE | [11 empty] | 28: FALSE; 30: FALSE; 32: FALSE; 34: FALSE; 36: FALSE; 38: FALSE; 40: FALSE; 42: FALSE; 44: FALSE; 46: FALSE; 48: FALSE; 50: FALSE; 52: FALSE; 54: FALSE; 56: FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  |  | FALSE |  | FALSE |  |  | FALSE |  | FALSE |  |  | FALSE |  | FALSE |  |  | FALSE
| 1 | TRUE | OR 1 | FALSE |  |  | FALSE |  | MU/A-HTG-CLG-H/RCV | MU/A-HTG-CLG-H/RCV | DRAW THRU C/C | DRAW THRU C/C | 8M | 8M | [11 empty] | 26: TRUE; 27: 0.9; 28: 0.78; 29: 0.25; 31: 1; 33: 0.75; 35: 1300; 37: 0.65; 39: 0.06; 41: 1.2; 43: 0; 45: 0.65; 47: 0.065; 49: 1.2 | A62 VRP |  | 0.333 |  | 1 |  | 0.0004 | 0.0004 | 0.015 | 0.015 | 0.7 | 0.75 | 0.7 | 0.72 | Calc |  | Calc | 5 |  | Calc |  | Calc | 13 |  | Calc |  | Calc | 12.5 | 5 | 0.013 | 0.0005 | Calc | 0.0099 | 0.0004 | 0.011
|  |  |  | TRUE |  |  | FALSE |  |  | FALSE |  | TRUE |  | TRUE | [11 empty] | 28: FALSE; 30: FALSE; 32: FALSE; 34: FALSE; 36: FALSE; 38: FALSE; 40: FALSE; 42: FALSE; 44: FALSE; 46: FALSE; 48: FALSE; 50: FALSE; 52: FALSE; 54: FALSE; 56: FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  | FALSE |  |  | FALSE |  | FALSE |  |  | FALSE |  | FALSE |  |  | FALSE |  | FALSE |  |  | FALSE
| 2 | TRUE | OR 2 | FALSE |  | Template MUA | TRUE |  | MU/A-HTG-CLG-H/RCV | MU/A-HTG-CLG-H/RCV | DRAW THRU C/C | DRAW THRU C/C | 8M | 8M | [11 empty] | 26: FALSE; 27: 0.7; 28: 0.78; 33: 0.65; 35: 2400; 37: 0.68; 43: 1500; 45: 0.62 | Flow Frac |  | 1 |  |  |  |  | 0.0004 |  | 0.015 | 0.72 | 0.75 | 0.71 | 0.72 | Calc |  | Calc | -6 |  | Calc |  | Calc |  |  | Calc |  | Calc |  | 5 | 0.013 | 0.0005 | Calc |  | 0.0004
|  |  |  | TRUE |  |  | FALSE |  | MU/A-HTG-CLG-H/RCV | FALSE | DRAW THRU C/C | TRUE | 8M | TRUE | [12 empty] | 0.88 | FALSE | 0.25 | FALSE | 1 | FALSE | 0.33 | FALSE | 1800 | FALSE | 0.65 | FALSE | 0.06 | FALSE | 1.2 | FALSE | 1200 | FALSE | 0.65 | FALSE | 0.065 | FALSE | 1.2 | FALSE |  | FALSE | 0 | FALSE | 0 | FALSE | Dsgn Frac | FALSE | 1 | FALSE | 1 | FALSE | 0.0004 | FALSE | 0.015 | FALSE | 0.7 | FALSE | 0.7 | FALSE | Calc | FALSE |  | 5 | FALSE | Calc | FALSE |  | 13 | FALSE | Calc | FALSE |  | 12.5 | FALSE | 0.013 | FALSE |  | 0.006 | FALSE | 0.011
Note on AE4: "Diversity" Diversity considers the reduction of internal loads from the zone level to the system level when sizing the system. This diversity occurs because we want to design zones for a worst case scenario but the probablility that all zones connected to a system will the incur full internal loads is low. This probability and even lower that the full loads occur at the same time. P. Henniger 2012-02-20
Note on AE6: Diversity: Lights Fraction to reduce internal cooling loads from what is specified at the zone to what is more probable at the system level. See general comments to the Diversity section. There is not normally much diversity for lighting systems unless there are multiple circuits fed from separate switches to change the lighting level, or for task lights. Task lights are accounted separately. P. Henniger 2012-02-20
Note on AG6: Diversity: Task Lights Fraction to reduce internal cooling loads from what is specified at the zone to what is more probable at the system level. See general comments to the Diversity section. Task lights are likely to see some diversity. P. Henniger 2012-02-20
Note on AI6: Diversity: Occupants Fraction to reduce internal cooling loads from what is specified at zones to what is more probable at the system level. See general comments to the Diversity section. Occupancy will have some diversity depending on the type of zones the system is serving. Be particularly vigilent in reducing loads for systems serving zones with high occupant density and low usage - meeting rooms, cafeteria etc. P. Henniger 2012-02-20
Note on AK6: Diversity: Equipment Fraction to reduce internal cooling loads from what is specified at the zone to what is more probable at the system level. See general comments to the Diversity section. Equipment (receptacle) load is probably the most overstimated of internal loads. There will almost always be considerable diversity from these loads. If you are using more than 0.50 for diversity factor you best have well substantiated sums for the operating power of the user's equipment. P. Henniger 2012-02-20
Note on AM6: "Fan T.S.P" Fan Total Static Pressure is an AMCA defined term and is used with Fan Static Efficiency to calculate Fan Shaft Power. If only Total Pressure is available from the fan curves, then you must use the Fan Total Efficiency in lieu of Fan Static Efficiency. P.Henniger - 2012-02-20
Note on AO6: "Static Efficiency" Enter the Static Ffficiency (or estimate) from the fan curve. See comment to "Fan T.S.P." P. Henniger 2012-02-20
Note on AQ6: "Drive Loss" Drive Loss (DL) ratio determines the (belt) drive loss to be added to the fan shaft power for detemining the motor output power. From a fan curve take the belt loss and divide by the fan shaft power. Motor output power = (1 + DL) x Fan Shaft Pwr. P. Henniger - 2012-02-20
Note on AS6: "Minimum Motor S.F." This field applies a Sizing Factor to the required power for selecting a minimum motor size for the fan. E.g if the motor output power required for a fan system is 4.3kW and a S.F.=1.25 is applied then the minimum motor size must provide 4.3 x 1.25 = 5.4kW. The motor selectied would be 5.5kW-(7.5hp). P. Henniger - 2012-02-20
Note on AU6: "Fan T.S.P" Fan Total Static Pressure is an AMCA defined term and is used with Fan Static Efficiency to calculate Fan Shaft Power. If only Total Pressure is available from the fan curves, then you must use the Fan Total Efficiency in lieu of Fan Static Efficiency. P.Henniger - 2012-02-20
Note on AW6: "Static Efficiency" Enter the Static Ffficiency (or estimate) from the fan curve. See comment to "Fan T.S.P." P. Henniger 2012-02-20
Note on AY6: "Drive Loss" Drive Loss (DL) ratio determines the (belt) drive loss to be added to the fan shaft power for detemining the motor output power. From a fan curve take the belt loss and divide by the fan shaft power. Motor output power = (1 + DL) x Fan Shaft Pwr. P. Henniger - 2012-02-20
Note on BA6: "Minimum Motor S.F." This field applies a Sizing Factor to the required power for selecting a minimum motor size for the fan. E.g if the motor output power required for a fan system is 4.3kW and a S.F.=1.25 is applied then the minimum motor size must provide 4.3 x 1.25 = 5.4kW. The motor selectied would be 5.5kW-(7.5hp). P. Henniger - 2012-02-20
Note on BC6: "Exhaust Air Calc Method" There are four methods available for determining exhaust air quantities. Exhaust air quantity needs to be considered for heat recovery performance, outdoor air ratio, and calculating fan power. L/s If the E/A quantity is known by calculation it can be entrerd directly rather than calulting This option is not available for Template Systems. =O/A Select this if an exhaust fan exhausts the O/A quantity directly and bypasses the heat recovery. Frac Dsgn As an approximation for early phases enter an exhaust flow as a fraction of the Dsgn S/A flow. For early design phases exhaust fans can be ignored if: They have relatively low static pressure and decent efficiency; It is known the exhaust quantity will not exceed the minimum O/A quantity; And if exhausts bypass heat recovery, the heat recovery effectiveness has adjusted to account for the imbalance of O/A and E/A. P. Henniger 2012-02-20
Note on BE6: "Exhaust Air Value" Enter the value corresponding. L/s If the E/A quantity is known by calculation it can be entrerd directly rather than calculating. This option is not available for Template Systems. =O/A Select this if a fan exhausts the O/A quantity directly and the exhast fan power needs to be quantified. Frac Dsgn As an approximation for early phases enter an exhaust flow as a fraction of the Dsgn S/A flow. For early design phases if dedicated exhaust fans have relatively low static pressure and decent efficiency, then their fan power can be approximated by assuming the E/A passes through the return air fan and this section can be ignored. If E/A does not pass through the heat recovery device then see comments under Heat Recovery. P. Henniger 2012-02-20
Note on BG6: "Average Power" For calculation of exhaust fan power. Often there is more than one exhaust fan serving an air handling system, and often exhaust fans will serve more than one air handling system. Inevitably you will have to come up with an average or a worst case. Enter the value in Watts per Litre/second of design airflow. P. Henniger 2012-02-20
Note on BJ6: "Minimum O/A Calculation" Minimum O/A is a critical design parameter and its calculation must be carefully considered. If you are not familiar with ASHRAE 62.1 or CSA Z317 for hospital projects, become familiar. A-62.1 AppA - refers to the Appendix A method in ASHRAE 62.1-2007 that takes into account multi-zone unvitiated outdoor air. This method is required if Zp is greater than 0.55. Use this for non-hospital projects. A-62.1 VRP - refers to the Ventilation Rate Procedure in the 2007 version of ASHRAE 62.1. Use this only if calculating outdoor air ratio for a baseline model where the Zp is greater than 0.55. Frac. Hrly - allows use of a minimum outdoor air ratio. Using this method implies that the minimum outdoor ratio (and damper) is fixed, and that the ratio has been determined by calculations in conformance with for A62.1 or CSA Z317. Frac. Design - allows use of a minimum outdoor air fraction. For this case this outdoor ratio air flow rate remains constant and equal to this fraction of the air systems's Design Supply AirFlow. Can only be used if outdoor air flow is measured. P. Henniger 2012-02-20.
Note on BL6: "Minimum O/A Ratio" This field is used when the Minimum O/A Calculation is Frac Flow. This is usually used with Hospitals following CSA Z317 that require a minimum outdoor air change for the zone. Because zones also have a minimum supply air change rate, this O/A ratio guarantees the minimum O/A flow is met. Value is 0.0 < O/A Ratio < 1.0. Usually 0.33 unless 100%O/A systems are used. P.Henniger 2012-02-20
Note on BN6: "Maximum O/A Ratio" This field is used to limit the O/A flow during Economizer (Free Cooling) mode. Important for sizing of humidifiers. P.Henniger 2013-02-14
Note on BP6: "Humidifier Leaving W" Enter the humidity ratio (W) of the S/A required to meet the room humidity criteria for spaces served by the air system. You will need a psychrometric chart or calculator. Typical values: 22C @ 30%RH is W=0.0048 22C @ 40%RH is W=0.0066 24C @ 30%RH is W=0.0055 24C @ 40%RH is W=0.0075 For psychrometrics formulas see ASHRAE Fundamentals 2009 pages 1.1-1.14 P. Henniger 2012-02-20
Note on BR6: "Humidifier Jacket Loss" The humidifier jacket's purpose is to prevent the humidifier from spitting condensate on the AHU floor and downstream components. The jacket encloses the humidifier manifold with steam to prevent cold air from condensing steam in the manifold and nozzles. There is a loss associated with this jacket. Enter it here as a ratio of the peak capacity. P. Henniger 2013-02-13
Note on BT6: "H/R Sensible Effectiveness" This field is provided to tell the esimulation engine there is a heat recovery device, and to calculate the entering air and humidity ratios to system components. Most manufacturers have a chart showing effectiveness as a function of air velocity through the device, E/A:O/A ratio, and rotational speed. P. Henniger 2013-02-13
Note on BW6: "H/R Latent Effectiveness" This field is provided to tell the esimulation engine there is a heat recovery device, and to calculate the entering air and humidity ratios to system components. Most manufacturers have a chart showing effectiveness as a function of air velocity through the device, E/A:O/A ratio, and rotational speed. P. Henniger 2013-02-13
Note on CB6: "Pre Heat Coil Leaving Air Temperature" Usually a preheat coil is provided to bring the outside air above freezing temperature to avoid damage to system components. Upstream of dessicant style heat recovery devices, the preheat coil may only heat to prevent frost on the recovery medium. This may be temperature may be significantly below freezing. If heat recovery failure is to be accommodated by the pre heat coil then this temperature entry needs to reflct that. P. Henniger 2012-02-20
Note on CG6: "Heating Coil Leaving Air Temperature" Enter the desired minimum supply air temperature desired under heating conditions. Note that if this is a draw thru system the H/C leaving air temperature will be lower due to fan heat gain and any temperature rise due to steam huumidification. Terminology: A true central heating raises the supply air temperature to above room temperature to allow heating by an air system. If there are reheat coils in the system, then the heating coil is really a preheat coil, or 2nd preheat coil. This is important in the control definitions for various simulation engines. P. Henniger 2012-02-20
Note on CL6: "Cooling Coil Leaving Air Temperature" Enter the desired minimum supply air temperature desired under cooling conditions. This temperature should be low enough to drive the apparatus dewpoint temperature low enough to dehumidify. Be cautious of draw-through systems. With heat gain from high static fans the C/C leaving air temperature will be substaitially suppressed resulting in larger cooling equipment and increased energy consumption. On the other hand, if the minimum S/A temperature required for cooling is chosen somewhat higher, the draw-thru fan can provide beneficial heat gain (reheat) without over dehumidifying the suppy air. P. Henniger 2012-02-20
Note on CQ6: "Cooling Coil Leaving Air Humidity Ratio (W)" Enter the desired C/C leaving air humidity ratio required to achieve the maximum humidity criteria of zones connected to the system. Consult a phychrometric chart or calculator. Typical values: 22C @ 50%RH is W=0.0082 22C @ 60%RH is W=0.0099 23C @ 50%RH is W=0.0087 23C @ 60%RH is W=0.0105 24C @ 50%RH is W=0.0093 24C @ 60%RH is W=0.0112 25C @ 50%RH is W=0.0099 25C @ 60%RH is W=0.0119 P. Henniger 2012-02-20

## D
|  |  | 2 | 3 | 4 | 6 | 7
BAD DATA | COMPONENT CONFIGURATION |  | 2 | 3 | 4 | 6 | 7 | 8 | 8 | 9 | 10 | No Choice |  | BLOW THRU C/C | [11 empty] | DRAW THRU C/C
↑ ! ↑ |  | 0 | [10 empty] | HHA System Type | 2 | 3 | 4 | 6 | 7 | 8 | 9 | [6 empty] | 2 | 3 | 4 | 6 | 7 | 8 | 9 | [9 empty] | OACalcType | EACalcType | OACalcType Template | EACalcType Template |  | NEMA Premium |  |  |  | NEMA HIGH EFFECIENCY | [8 empty] | TEFC PremiumMotors | [6 empty] | ODP Premium Motors
| 0 | [11 empty] | REC-HTG-ONLY | 1A | 1B | [10 empty] | REC-HTG-ONLY | 1C | 1D | [10 empty] | REC-HTG-ONLY | 1 | BLOW THRU H/C | DRAW THRU H/C | A62 VRP |  | A62 VRP |  |  |  |  | 2 POLE | 4 POLE | 6 POLE | 8 POLE | 2 POLE | 4 POLE | 6 POLE | 8 POLE |  |  |  | 2 POLE |  | 4 POLE |  | 6 POLE |  |  |  | 2 POLE |  | 4 POLE |  | 6 POLE
[13 empty] | REC-CLG | 2A | 2C | [10 empty] | REC-CLG | 2E | 2G | [10 empty] | REC-CLG | 2 | BLOW THRU C/C | DRAW THRU C/C | Flow Frac | Dsgn Frac | Flow Frac | Dsgn Frac | Pulldown window | kW | hp | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  |  | 3 | 4 | 5 | 6 | 7 | 8 |  |  | 3 | 4 | 5 | 6 | 7 | 8
|  | 1A | ←E/A | MIX | FAN | R/A ← | [6 empty] | REC-HTG-CLG | 3A | 3B | 3C | 3J | 3K | 3L | [6 empty] | REC-HTG-CLG | 3D | 3E | 3F | 3M | 3N | 3P | [6 empty] | REC-HTG-CLG | 3 | BLOW THRU C/C | DRAW THRU C/C | Dsgn Frac | =O/A | Dsgn Frac | =O/A | 0.75 | 0.75 | 1 | 75.5 | 82.5 | 80 | 74 | 75.5 | 82.5 | 80 | 74 | A | 0.75 | 1 | 77 | 74 | 85.5 | 82.5 | 82.5 | 80 | 0.75 | 1 | 77 | 74 | 85.5 | 82.5 | 82.5 | 80 | 0.75
| 1A |  | S/A → | MIX | FAN | H/C | HUM | S/A → |  |  |  |  | REC-HTG-H/RCV | 4A | 4C | [10 empty] | REC-HTG-H/RCV | 4B | 4D | [10 empty] | REC-HTG-H/RCV | 4 | BLOW THRU H/C | DRAW THRU H/C |  | L/s |  |  | 1.1 | 1.1 | 1.5 | 82.5 | 84 | 84 | 75.5 | 82.5 | 84 | 85.5 | 77 | B | 1.1 | 1.5 | 84 | 81.5 | 86.5 | 84 | 87.5 | 85.5 | 1.1 | 1.5 | 84 | 81.5 | 86.5 | 84 | 86.5 | 84 | 1.1
[13 empty] | REC-HTG-CLG-H/RCV | 5A | 5B | 5C | 5G | 5H | 5J | 5N | 5P | 5Q | 5U | 5V | 5W | REC-HTG-CLG-H/RCV | 5D | 5E | 5F | 5K | 5L | 5M | 5R | 5S | 5T | 5X | 5Y | 5Z | REC-HTG-CLG-H/RCV | 5 | BLOW THRU C/C | DRAW THRU C/C |  |  |  |  | 1.5 | 1.5 | 2 | 84 | 84 | 85.5 | 85.5 | 84 | 84 | 85.5 | 82.5 | C | 1.5 | 2 | 85.5 | 82.5 | 86.5 | 84 | 88.5 | 86.5 | 1.5 | 2 | 85.5 | 82.5 | 86.5 | 84 | 87.5 | 85.5 | 1.5
|  | 1B | ←E/A | - | MIX | FAN | R/A ← | [5 empty] | MU/A-HTG-ONLY | 6A | 6C | [10 empty] | MU/A-HTG-ONLY | 6B | 6D | [10 empty] | MU/A-HTG-ONLY | 6 | BLOW THRU H/C | [5 empty] | 2.2 | 2.2 | 3 | 84 | 84 | 86.5 | 86.5 | 85.5 | 84 | 87.5 | 84 | D | 2.2 | 3 | 86.5 | 84 | 89.5 | 87.5 | 89.5 | 87.5 | 2.2 | 3 | 85.5 | 82.5 | 89.5 | 87.5 | 88.5 | 86.5 | 2.2
| 1B |  | → O/A | PH/C | MIX | FAN | H/C | HUM | S/A → |  |  |  | MU/A-HTG-H/RCV | 7A | [11 empty] | MU/A-HTG-H/RCV | 7B | [11 empty] | MU/A-HTG-H/RCV | 7 | BLOW THRU H/C | [5 empty] | 3.75 | 3.75 | 5 | 85.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 85.5 | E | 3.75 | 5 | 88.5 | 86.5 | 89.5 | 87.5 | 89.5 | 87.5 | 3.75 | 5 | 86.5 | 84 | 89.5 | 87.5 | 89.5 | 87.5 | 3.75
[13 empty] | MU/A-HTG-CLG-H/RCV | 8A | 8B | 8C | [9 empty] | MU/A-HTG-CLG-H/RCV | 8M | [11 empty] | MU/A-HTG-CLG-H/RCV | 8 | BLOW THRU C/C | DRAW THRU C/C |  |  |  |  | 5.5 | 5.5 | 7.5 | 87.5 | 88.5 | 88.5 | 88.5 | 88.5 | 89.5 | 89.5 | 85.5 | F | 5.5 | 7.5 | 89.5 | 87.5 | 91.7 | 90.2 | 91 | 89.5 | 5.5 | 7.5 | 88.5 | 86.5 | 91 | 89.5 | 90.2 | 88.5 | 5.5
|  | 1C | ←E/A | MIX | FAN | R/A ← | [40 empty] | 7.5 | 7.5 | 10 | 88.5 | 89.5 | 90.2 | 89.5 | 89.5 | 89.5 | 89.5 | 88.5 | G | 7.5 | 10 | 90.2 | 88.5 | 91.7 | 90.2 | 91 | 89.5 | 7.5 | 10 | 89.5 | 87.5 | 91.7 | 90.2 | 91.7 | 90.2 | 7.5
| 1C |  | → O/A | MIX | H/C | HUM | FAN | S/A → | [38 empty] | 11 | 11 | 15 | 89.5 | 91 | 90.2 | 89.5 | 90.2 | 91 | 90.2 | 88.5 | H | 11 | 15 | 91 | 89.5 | 92.4 | 91 | 91.7 | 90.2 | 11 | 15 | 90.2 | 88.5 | 93 | 91.7 | 91.7 | 90.2 | 11
[47 empty] | 15 | 15 | 20 | 90.2 | 91 | 91 | 90.2 | 90.2 | 91 | 90.2 | 89.5 | I | 15 | 20 | 91 | 89.5 | 93 | 91.7 | 91.7 | 90.2 | 15 | 20 | 91 | 89.5 | 93 | 91.7 | 92.4 | 91 | 15
|  | 1D | ←E/A | - | MIX | FAN | R/A ← | [39 empty] | 18.5 | 18.5 | 25 | 91 | 91.7 | 91.7 | 90.2 | 91 | 92.4 | 91.7 | 89.5 | J | 18.5 | 25 | 91.7 | 90.2 | 93.6 | 92.4 | 93 | 91.7 | 18.5 | 25 | 91.7 | 90.2 | 93.6 | 92.4 | 93 | 91.7 | 18.5
| 1D |  | → O/A | PH/C | MIX | H/C | HUM | FAN | S/A → | [37 empty] | 22 | 22 | 30 | 91 | 92.4 | 92.4 | 91 | 91 | 92.4 | 91.7 | 91 | K | 22 | 30 | 91.7 | 90.2 | 93.6 | 92.4 | 93 | 91.7 | 22 | 30 | 91.7 | 90.2 | 94.1 | 93 | 93.6 | 92.4 | 22
[47 empty] | 30 | 30 | 40 | 91.7 | 93 | 93 | 91 | 91.7 | 93 | 93 | 91 | L | 30 | 40 | 92.4 | 91 | 94.1 | 93 | 94.1 | 93 | 30 | 40 | 92.4 | 91 | 94.1 | 93 | 94.1 | 93 | 30
|  | 2A | ←E/A | MIX | FAN | R/A ← | [40 empty] | 37 | 37 | 50 | 92.4 | 93 | 93 | 91.7 | 92.4 | 93 | 93 | 91.7 | M | 37 | 50 | 93 | 91.7 | 94.5 | 93.6 | 94.1 | 93 | 37 | 50 | 93 | 91.7 | 94.5 | 93.6 | 94.1 | 93 | 37
| 2A |  | → O/A | MIX | FAN | HUM | C/C | S/A → | [38 empty] | 45 | 45 | 60 | 93 | 93.6 | 93.6 | 92.4 | 93 | 93.6 | 93.6 | 91.7 | N | 45 | 60 | 93.6 | 92.4 | 95 | 94.1 | 94.5 | 93.6 | 45 | 60 | 93.6 | 92.4 | 95 | 94.1 | 94.5 | 93.6 | 45
[47 empty] | 55 | 55 | 75 | 93 | 94.1 | 93.6 | 93.6 | 93 | 94.1 | 93.6 | 93 | O | 55 | 75 | 93.6 | 92.4 | 95.4 | 94.5 | 94.5 | 93.6 | 55 | 75 | 93.6 | 92.4 | 95 | 94.1 | 94.5 | 93.6 | 55
|  | 2B | [44 empty] | 75 | 75 | 100 | 93 | 94.1 | 94.1 | 93.6 | 93.6 | 94.5 | 94.1 | 93 | P | 75 | 100 | 94.1 | 93 | 95.4 | 94.5 | 95 | 94.1 | 75 | 100 | 93.6 | 92.4 | 95.4 | 94.5 | 95 | 94.1 | 75
| 2B | [45 empty] | 90 | 90 | 125 | 93.6 | 94.5 | 94.1 | 93.6 | 94.5 | 94.5 | 94.1 | 93.6 | Q | 90 | 125 | 95 | 94.1 | 95.4 | 94.5 | 95 | 94.1 | 90 | 125 | 94.1 | 93 | 95.4 | 94.5 | 95 | 94.1 | 90
|  | 2C | ←E/A | - | MIX | FAN | R/A ←
| 2C |  | → O/A | PH/C | MIX | FAN | HUM | C/C | S/A →
2D
2D
|  | 2E | ←E/A | MIX | FAN | R/A ←
| 2E |  | → O/A | MIX | HUM | C/C | FAN | S/A →
2F
2F
|  | 2G | ←E/A | - | MIX | FAN | R/A ←
| 2G |  | → O/A | PH/C | MIX | HUM | C/C | FAN | S/A →
2H
2H
|  | 3A | ←E/A | MIX | FAN | R/A ←
| 3A |  | → O/A | MIX | FAN | C/C | H/C | HUM | S/A →
|  | 3B | ←E/A | MIX | FAN | R/A ←
| 3B |  | → O/A | MIX | FAN | H/C | HUM | C/C | S/A →
|  | 3C | ←E/A | MIX | FAN | R/A ←
| 3C |  | → O/A | MIX | H/C | HUM | FAN | C/C | S/A →
|  | 3D | ←E/A | MIX | FAN | R/A ←
| 3D |  | → O/A | MIX | C/C | FAN | H/C | HUM | S/A →
|  | 3E | ←E/A | MIX | FAN | R/A ←
| 3E |  | → O/A | MIX | C/C | H/C | HUM | FAN | S/A →
|  | 3F | ←E/A | MIX | FAN | R/A ←
| 3F |  | → O/A | MIX | H/C | HUM | C/C | FAN | S/A →
|  | 3G | ←E/A | - | - | - | - | R/A ←
| 3G |  | → O/A | - | - | - | - | - | S/A →
|  | 3H | ←E/A | - | - | - | - | R/A ←
| 3H |  | → O/A | - | - | - | - | - | S/A →
|  | 3J | ←E/A | - | MIX | FAN | R/A ←
| 3J |  | → O/A | PH/C | MIX | FAN | C/C | H/C | HUM | S/A →
|  | 3K | ←E/A | - | MIX | FAN | R/A ←
| 3K |  | → O/A | PH/C | MIX | FAN | H/C | HUM | C/C | S/A →
|  | 3L | ←E/A | - | MIX | FAN | R/A ←
| 3L |  | → O/A | PH/C | MIX | H/C | HUM | FAN | C/C | S/A →
|  | 3M | ←E/A | - | MIX | FAN | R/A ←
| 3M |  | → O/A | PH/C | MIX | C/C | FAN | H/C | HUM | S/A →
|  | 3N | ←E/A | - | MIX | FAN | R/A ←
| 3N |  | → O/A | PH/C | MIX | C/C | H/C | HUM | FAN | S/A →
|  | 3P | ←E/A | - | MIX | FAN | R/A ←
| 3P |  | → O/A | PH/C | MIX | H/C | HUM | C/C | FAN | S/A →
|  | 4A | ←E/A | FAN | H/R | MIX | R/A ←
| 4A |  | → O/A | - | H/R | MIX | FAN | H/C | HUM | S/A →
|  | 4B | ←E/A | FAN | H/R | MIX | R/A ←
| 4B |  | → O/A | - | H/R | MIX | H/C | HUM | FAN | S/A →
|  | 4C | ←E/A | FAN | H/R | MIX | R/A ←
| 4C |  | → O/A | PH/C | H/R | MIX | FAN | H/C | HUM | S/A →
|  | 4D | ←E/A | FAN | H/R | MIX | R/A ←
| 4D |  | → O/A | PH/C | H/R | MIX | H/C | HUM | FAN | S/A →
|  | 5A | ←E/A | FAN | H/R | MIX | R/A ←
| 5A |  | → O/A | - | H/R | MIX | FAN | C/C | H/C | HUM | S/A →
|  | 5B | → O/A: ←E/A; -: FAN; H/R: H/R; MIX: MIX; FAN: R/A ←
| 5B |  | → O/A | - | H/R | MIX | FAN | H/C | HUM | C/C | S/A →
|  | 5C | → O/A: ←E/A; -: FAN; H/R: H/R; MIX: MIX; FAN: R/A ←
| 5C |  | → O/A | - | H/R | MIX | H/C | HUM | FAN | C/C | S/A →
|  | 5D | → O/A: ←E/A; -: FAN; H/R: H/R; MIX: MIX; H/C: R/A ←
| 5D |  | → O/A | - | H/R | MIX | C/C | FAN | H/C | HUM | S/A →
|  | 5E | → O/A: ←E/A; -: FAN; H/R: H/R; MIX: MIX; C/C: R/A ←
| 5E |  | → O/A | - | H/R | MIX | C/C | H/C | HUM | FAN | S/A →
|  | 5F | → O/A: ←E/A; -: FAN; H/R: H/R; MIX: MIX; C/C: R/A ←
| 5F |  | → O/A | - | H/R | MIX | H/C | HUM | C/C | FAN | S/A →
|  | 5G | → O/A: ←E/A; -: FAN; H/R: H/R; MIX: MIX; H/C: R/A ←
| 5G |  | → O/A | PH/C | H/R | MIX | FAN | C/C | H/C | HUM | S/A →
|  | 5H | → O/A: ←E/A; PH/C: FAN; H/R: H/R; MIX: MIX; FAN: R/A ←
| 5H |  | → O/A | PH/C | H/R | MIX | FAN | H/C | HUM | C/C | S/A →
|  | 5J | → O/A: ←E/A; PH/C: FAN; H/R: H/R; MIX: MIX; FAN: R/A ←
| 5J |  | → O/A | PH/C | H/R | MIX | H/C | HUM | FAN | C/C | S/A →
|  | 5K | → O/A: ←E/A; PH/C: FAN; H/R: H/R; MIX: MIX; H/C: R/A ←
| 5K |  | → O/A | PH/C | H/R | MIX | C/C | FAN | H/C | HUM | S/A →
|  | 5L | → O/A: ←E/A; PH/C: FAN; H/R: H/R; MIX: MIX; C/C: R/A ←
| 5L |  | → O/A | PH/C | H/R | MIX | C/C | H/C | HUM | FAN | S/A →
|  | 5M | → O/A: ←E/A; PH/C: FAN; H/R: H/R; MIX: MIX; C/C: R/A ←
| 5M |  | → O/A | PH/C | H/R | MIX | H/C | HUM | C/C | FAN | S/A →
|  | 5N | → O/A: ←E/A; PH/C: MIX; H/R: FAN; MIX: H/R; H/C: R/A ←
| 5N |  | → O/A | MIX | - | H/R | FAN | C/C | H/C | HUM | S/A →
|  | 5P | → O/A: ←E/A; MIX: MIX; -: FAN; H/R: H/R; FAN: R/A ←
| 5P |  | → O/A | MIX | - | H/R | FAN | H/C | HUM | C/C | S/A →
|  | 5Q | → O/A: ←E/A; MIX: MIX; -: FAN; H/R: H/R; FAN: R/A ←
| 5Q |  | → O/A | MIX | - | H/R | H/C | HUM | FAN | C/C | S/A →
|  | 5R | → O/A: ←E/A; MIX: MIX; -: FAN; H/R: H/R; H/C: R/A ←
| 5R |  | → O/A | MIX | - | H/R | C/C | FAN | H/C | HUM | S/A →
|  | 5S | → O/A: ←E/A; MIX: MIX; -: FAN; H/R: H/R; C/C: R/A ←
| 5S |  | → O/A | MIX | - | H/R | C/C | H/C | HUM | FAN | S/A →
|  | 5T | → O/A: ←E/A; MIX: MIX; -: FAN; H/R: H/R; C/C: R/A ←
| 5T |  | → O/A | MIX | - | H/R | H/C | HUM | C/C | FAN | S/A →
|  | 5U | → O/A: ←E/A; MIX: MIX; -: FAN; H/R: H/R; H/C: R/A ←
| 5U |  | → O/A | MIX | PH/C | H/R | FAN | C/C | H/C | HUM | S/A →
|  | 5V | → O/A: ←E/A; MIX: MIX; PH/C: FAN; H/R: H/R; FAN: R/A ←
| 5V |  | → O/A | MIX | PH/C | H/R | FAN | H/C | HUM | C/C | S/A →
|  | 5W | → O/A: ←E/A; MIX: MIX; PH/C: FAN; H/R: H/R; FAN: R/A ←
| 5W |  | → O/A | MIX | PH/C | H/R | H/C | HUM | FAN | C/C | S/A →
|  | 5X | → O/A: ←E/A; MIX: MIX; PH/C: FAN; H/R: H/R; H/C: R/A ←
| 5X |  | → O/A | MIX | PH/C | H/R | C/C | FAN | H/C | HUM | S/A →
|  | 5Y | → O/A: ←E/A; MIX: MIX; PH/C: FAN; H/R: H/R; C/C: R/A ←
| 5Y |  | → O/A | MIX | PH/C | H/R | C/C | H/C | HUM | FAN | S/A →
|  | 5Z | → O/A: ←E/A; MIX: MIX; PH/C: FAN; H/R: H/R; C/C: R/A ←
| 5Z |  | → O/A | MIX | PH/C | H/R | H/C | HUM | C/C | FAN | S/A →
|  | 6A | → O/A: ←E/A; MIX: FAN; PH/C: R/A ←
| 6A |  | → O/A: → O/A; MIX: FAN; PH/C: H/C; H/R: HUM; H/C: S/A →
|  | 6B | → O/A: ←E/A; MIX: FAN; PH/C: R/A ←
| 6B |  | → O/A: → O/A; MIX: H/C; PH/C: HUM; H/R: FAN; H/C: S/A →
|  | 6C | → O/A: ←E/A; MIX: FAN; PH/C: R/A ←
| 6C |  | → O/A | PH/C | FAN | H/C | HUM | S/A →
|  | 6D | → O/A: ←E/A; MIX: FAN; PH/C: R/A ←
| 6D |  | → O/A | PH/C | H/C | HUM | FAN | S/A →
|  | 7A | → O/A: ←E/A; MIX: FAN; PH/C: H/R; H/R: R/A ←
| 7A |  | → O/A | - | H/R | FAN | H/C | HUM | S/A →
|  | 7B | → O/A: ←E/A; MIX: FAN; PH/C: H/R; H/R: R/A ←
| 7B |  | → O/A | - | H/R | H/C | HUM | FAN | S/A →
|  | 7C | → O/A: ←E/A; MIX: FAN; PH/C: H/R; H/R: R/A ←
| 7C |  | → O/A | PH/C | H/R | FAN | H/C | HUM | S/A →
|  | 7D | → O/A: ←E/A; MIX: FAN; PH/C: H/R; H/R: R/A ←
| 7D |  | → O/A | PH/C | H/R | H/C | HUM | FAN | S/A →
|  | 7E | → O/A: ←E/A; MIX: FAN; PH/C: H/R; H/R: R/A ←
| 7E |  | → O/A | - | H/R | FAN | H/C | HUM | S/A →
|  | 7F | → O/A: ←E/A; MIX: FAN; PH/C: H/R; H/R: R/A ←
| 7F |  | → O/A | - | H/R | H/C | HUM | FAN | S/A →
|  | 7G | ←E/A | - | - | - | - | R/A ←
| 7G |  | → O/A | - | - | - | - | - | - | - | S/A →
|  | 7H | ←E/A | - | - | - | - | R/A ←
| 7H |  | → O/A | - | - | - | - | - | - | - | S/A →
|  | 8A | → O/A: ←E/A; MIX: FAN; PH/C: H/R; H/R: R/A ←
| 8A |  | → O/A | - | H/R | FAN | C/C | H/C | HUM | S/A →
|  | 8B | → O/A: ←E/A; -: FAN; H/R: H/R; FAN: R/A ←
| 8B |  | → O/A | - | H/R | FAN | H/C | HUM | C/C | S/A →
|  | 8C | → O/A: ←E/A; -: FAN; H/R: H/R; FAN: R/A ←
| 8C |  | → O/A | - | H/R | H/C | HUM | FAN | C/C | S/A →
|  | 8D | → O/A: ←E/A; -: FAN; H/R: H/R; H/C: R/A ←
| 8D |  | → O/A | - | H/R | C/C | FAN | H/C | HUM | S/A →
|  | 8E | → O/A: ←E/A; -: FAN; H/R: H/R; C/C: R/A ←
| 8E |  | → O/A | - | H/R | C/C | H/C | HUM | FAN | S/A →
|  | 8F | → O/A: ←E/A; -: FAN; H/R: H/R; C/C: R/A ←
| 8F |  | → O/A | - | H/R | H/C | HUM | C/C | FAN | S/A →
|  | 8G | → O/A: ←E/A; -: FAN; H/R: H/R; H/C: R/A ←
| 8G |  | → O/A | PH/C | H/R | FAN | C/C | H/C | HUM | S/A →
|  | 8H | → O/A: ←E/A; PH/C: FAN; H/R: H/R; FAN: R/A ←
| 8H |  | → O/A | PH/C | H/R | FAN | H/C | HUM | C/C | S/A →
|  | 8J | → O/A: ←E/A; PH/C: FAN; H/R: H/R; FAN: R/A ←
| 8J |  | → O/A | PH/C | H/R | H/C | HUM | FAN | C/C | S/A →
|  | 8K | → O/A: ←E/A; PH/C: FAN; H/R: H/R; H/C: R/A ←
| 8K |  | → O/A | PH/C | H/R | C/C | FAN | H/C | HUM | S/A →
|  | 8L | → O/A: ←E/A; PH/C: FAN; H/R: H/R; C/C: R/A ←
| 8L |  | → O/A | PH/C | H/R | C/C | H/C | HUM | FAN | S/A →
|  | 8M | → O/A: ←E/A; PH/C: FAN; H/R: H/R; C/C: R/A ←
| 8M |  | → O/A | PH/C | H/R | H/C | HUM | C/C | FAN | S/A →