## Sheet1
|  | floor |  |  | Zone # | Zone TemplGroup | Zone TemplGroup Prev | Zone TemplName | Zone TemplName Prev |  | Area | Ceiling Height | Location |  |  | Max Ceiling | Max Ceiling Prev | Dsn Space Clg Temp | Dsn Space Clg Temp Prev | Dsn Space Clg RH | Dsn Space Clg RH Prev | Dsn Space Htg Temp | Dsn Space Htg Temp Prev | Dsn Space Htg RH | Dsn Space Htg RH Prev | Dsn SA Clg Temp | Dsn SA Clg Temp Prev | Dsn SA Clg Humid | Dsn SA Clg Humid Prev | Dsn SA Htg Temp | Dsn SA Htg Temp Prev | Dsn SA Htg Humid | Dsn SA Htg Humid Prev | Min OA ACH | Min OA ACH Prev | Min OA Rp | Min OA Rp Prev | Min OA Ra | Min OA Ra Prev | OA EZ Vent Eff | OA EZ Vent Eff Prev | Min SA L/S/m2 | Min SA L/S/m2 Prev | Min SA ACH | Min SA ACH Prev | Min Exh L/S | Min Exh L/S Prev | Min Exh ACH | Min Exh ACH Prev | Inf Clg Dsn ACH | Inf Clg Dsn ACH Prev | Inf Clg Dsn L/S/m2 | Inf Clg Dsn L/S/m2 Prev | Inf Htg Dsn ACH | Inf Htg Dsn ACH Prev | Inf Htg Dsn L/S/m2 | Inf Htg Dsn L/S/m2 Prev | Light Pwr | Light Pwr Prev | Light Unit | Light Unit Prev | Light %RA | Light %RA Prev | TaskLgt Pwr | TaskLgt Pwr Prev | TaskLgt Unit | TaskLgt Unit Prev | Occ Num | Occ Num Prev | Occ Unit | Occ Unit Prev | Occ Met | Occ Met Prev | Occ SHR | Occ SHR Prev | Equip Pwr | Equip Pwr Prev | Equip Unit | Equip Unit Prev | Equip SHR | Equip SHR Prev
ZONE HVAC LOADS: Input Data | [15 empty] | Project Name: | [53 empty] | Edit Date: |  |  |  | 2013.3.27 12:54
ZONE INFORMATION | [13 empty] | TEMPERATURE - HUMIDITY - AIRFLOW | [43 empty] | INTERNAL GAINS
System |  |  | Location |  |  | Template | [27 empty] | Min O/A | [7 empty] | Min S/A | [7 empty] | Infiltration | [7 empty] | Lights | [5 empty] | Task Lgt |  |  |  | Occupancy | [7 empty] | Equip
# | Name |  | Flr/Blk Zn # | Type Location | Zone Name | Group |  | Name |  |  | Area/Ceiling |  |  |  |  | Max. Ceiling |  | Design Space Temperature & Humidity Clng Htng | [7 empty] | Design Supply Temperature & Humidity Clng Htng | [7 empty] | Min |  | RP |  | RA |  | EZ |  | Min Flow |  |  |  | Exh Flow |  |  |  | Clng Dsn |  |  |  | Htng Dsn |  |  |  | Pwr |  | Unit |  | Frac RA |  | Pwr |  | Unit |  | Occ |  | Unit |  | Met |  | SHR |  | Pwr |  | Unit |  | SHR
[11 empty] | m2 m |  |  |  |  | m |  | oC |  | % RH |  | oC |  | % RH |  | oC |  | KgH2O/KgDryAir |  | oC |  | KgH2O/KgDryAir |  | AC/h |  | L/s occ |  | L/s/ m2 |  |  |  | L/s/ m2 |  | AC/h |  | L/s |  | AC/h |  | AC/h |  | L/s/m2 wall |  | AC/h |  | L/s/m2 wall | [15 empty] | W/ occ
HHA ZONE, Field 13: System# | From Systems Sheet, Lookup function |  | HHA ZONE , Field 1: Zone # | HHA ZONE Field 3, [Hard Return] Field 16 | HHA ZONE, Field 2: Zone Name ! Field 11 Room Name | From Template Sheet, Lookup function |  |  | HHA ZONE Field 12: Template # |  | HHA ZONE Field 14: Ceiling Height/1000 | HHA ZONE, Field 5, Area/1 000 000 | [47 empty] | W/Occ | [5 empty] | W/Occ |  |  |  | m2/occ | [7 empty] | W/Occ
1 |  | f12D | 12-D | COND | Zn.01 | GENERAL | SURGERY | Clean utility | Minor Surgery | GENERAL : Clean utility | 400 | 3.2 | EXT |  |  | 3.2 |  | 24 |  | 60 |  | 22 |  | 30 |  | 14 |  | 0.0085 |  | 40 |  | 0.008 |  | 2 |  | 2.5 |  | 0.3 |  | 1 |  |  |  | 6 |  |  |  | 1 |  | 0 |  |  |  | 0.5 |  |  |  | 1.12 |  | W/m2 |  | 0.1 |  |  |  | W/m2 |  | 100 |  | occ |  | 117 |  | 0.577 |  | 1.32 |  | W/m2 |  | 0.5
|  |  | 1 | EXT | [10 empty] | Templ: | W/m2 | - | 24 | - | 60 | - | 22 | - | 30 | - | 14 | - | 0.0085 | - | 40 | - | 0.008 | - | 2 | - | 2.5 | - | 0.3 | - | 1 | - | 12 | - | 6 | - | 25 | - | 1 | - | 0 | - | 0.05 | - | 0.5 | - | 0.05 | - | 1.12 | - | W/m2 | - | 0.1 | - | 0.5 | - | W/m2 | - | 0.21 | - | m2/occ | - | 120 | - | 0.577 | - | 1.32 | - | W/m2 | - | 0.5 | -
1 |  | f12D | 12-D | COND | Zn.02 | GENERAL | SURGERY | Soiled Utility | Minor Surgery | GENERAL : Soiled Utility | 400 | 3.2 | EXT |  |  | 3.2 | [5 empty] | 22 |  | 30 |  | 14 |  | 0.0085 |  | 40 |  | 0.008 |  | 2 |  | 2.5 |  | 0.3 |  | 1 |  | 20 |  |  |  | 50 | [5 empty] | 0.05 |  |  |  | 0.05 |  | 1 |  | W/occ |  | 0.2 |  |  |  | W/occ |  | 1 |  | occ/m2 |  | 117 |  | 0.577 |  | 1 |  | W/occ |  | 0.5
|  |  | 2 | EXT | [10 empty] | Templ: | W/m2 | - | 24 | - | 60 | - | 22 | - | 30 | - | 14 | - | 0.0085 | - | 40 | - | 0.008 | - | 0 | - | 2.5 | - | 0.3 | - | 1 | - | 12 | - | 10 | - | 25 | - | 1 | - | 0 | - | 0.05 | - | 0.5 | - | 0.05 | - | 1.11 | - | W/m2 | - | 0.1 | - | 0.5 | - | W/m2 | - | 0.2 | - | m2/occ | - | 120 | - | 0.577 | - | 1.31 | - | W/m2 | - | 0.5 | -
1 |  | f12D | 12-D | COND | Zn.03 | GENERAL | SURGERY | Medication Room | Minor Surgery | GENERAL : Medication Room | 400 | 3.2 | EXT |  |  | 3.2
|  |  | 3 | EXT | [10 empty] | Templ: | W/m2 | - | 24 | - | 60 | - | 22 | - | 30 | - | 14 | - | 0.0085 | - | 40 | - | 0.008 | - | 2 | - | 2.5 | - | 0.3 | - | 1 | - | 12 | - | 6 | - | 25 | - | 1 | - | 0 | - | 0.05 | - | 0.5 | - | 0.05 | - | 1.13 | - | W/m2 | - | 0.1 | - | 0.5 | - | W/m2 | - | 0.22 | - | m2/occ | - | 120 | - | 0.577 | - | 1.33 | - | W/m2 | - | 0.5 | -
1 |  | f12D | 12-D | COND | Zn.04 | GENERAL | SURGERY | Corridors | Minor Surgery | GENERAL : Corridors | 400 | 3.2 | EXT |  |  | 3.2 |  | 20 |  | 50 |  | 20 |  | 50 |  | 12 |  | 0.007 |  | 36 |  | 0.006 |  |  |  | 2.4 |  | 0.2 |  | 0.8 |  | 10 |  | 2 |  | 22 |  | 1 |  | 0.1 |  | 0.04 |  | 0.4 |  | 0.04 |  | 100 |  | W |  |  |  | 50 |  | W |  | 5 |  | occ |  | 150 |  | 0.777 |  | 80 |  | W
|  |  | 4 | EXT | [10 empty] | Templ: | W/m2 | - | 24 | - | 60 | - | 20 | - | 30 | - | 14 | - | 0.0085 | - | 40 | - | 0.008 | - | 1 | - | 2.5 | - | 0.3 | - | 1 | - | 12 | - | 3 | - | 25 | - | 1 | - | 0 | - | 0.05 | - | 0.5 | - | 0.05 | - | 1.14 | - | W/m2 | - | 0.1 | - | 0.5 | - | W/m2 | - | 0.23 | - | m2/occ | - | 120 | - | 0.577 | - | 1.34 | - | W/m2 | - | 0.5 | -
1 |  | f12D | 12-D | COND | Zn.05 | GENERAL | SURGERY | Dining | Minor Surgery | GENERAL : Dining | 400 | 3.2 | EXT |  |  | 3.2 |  | 24 |  | 60 | [5 empty] | 14 |  | 0.0085 |  | 40 |  | 0.008 |  | 2 | [9 empty] | 7 | [9 empty] | 0.6 |  |  |  | 1.2 |  |  |  | 0.1 |  |  |  | W/occ |  | 7 |  |  |  | 117 |  |  |  | 1.19 |  |  |  | 0.7
|  |  | 5 | EXT | [10 empty] | Templ: | W/m2 | - | 24 | - | 60 | - | 20 | - | 30 | - | 14 | - | 0.0085 | - | 40 | - | 0.008 | - | 2 | - | 2.5 | - | 0.3 | - | 1 | - | 12 | - | 6 | - | 25 | - | 1 | - | 0 | - | 0.05 | - | 0.5 | - | 0.05 | - | 1.23 | - | W/m2 | - | 0.1 | - | 0.5 | - | W/m2 | - | 0.32 | - | m2/occ | - | 120 | - | 0.577 | - | 1.43 | - | W/m2 | - | 0.5 | -